Power Fang Enterprise Company Ltd

Professional fluid control field

JS-03

JS-01

JS-02

JS-04H with butterly valve

JS-02 (2)

JS-02 (3)

JS-01 with ball valve

JS-06H

JS-05H

JS-04

JS-03H

JS-03

Power Fang Enterprise Company Ltd

The information of the specifications & the features

| Operation Voltage of Various Types | Standard ON/OFF Type | “Low Energy” ON/OFF Type | “Fast Acting” ON/OFF Type |
| --- | --- | --- | --- |
|  | 12 VDC 24 VDC 24 VAC/DC 110/220 VAC (1-Phase) 220/380/440/460 VAC (3-Phase) | 110/220 VAC (1-Phase) | 12 VDC 24 VDC 24 VAC/DC 110/220 VAC (1-Phase) |
|  | Modulation Type | “Battery Backup Fail-safe” ON/OFF Type |  |
|  | 24/110/220 VAC (1-Phase) | 12 VDC 24 VAC/DC 110/220 VAC (1-Phase) |  |
| Protection Class | IP 67 according to STD. IEC 60529 |  |  |
| Working Condition | Ambient Temperature: -10 to 60°C (14 to 140°F) The humidity: 30% ~ 95% |  |  |
| Rotation Angle | 0~270° |  |  |
| Enclosure | Case Material：Aluminum alloy Cover Material：Polycarbonate |  |  |
| Certiﬁcation / Test | Comply with CE directives of - The LOW Voltage Directive, 73/23/EEC, 93/68 EEC - The EMC Directive, 89/336/EEC |  |  |
| Mounting Flange | ISO 5211 |  |  |
| Conduit Entrance | 1/2"PF |  |  |
| Accessory | -Cable gland(IP68) x 1 p(Cable range: Ø10~6mm) -Protection for manual lever – rubber cover |  |  |
| Optional Items | -Space heater -Additional limit switches x2 (250VAC / 0.1A) -Built -in LED position indicator -Modulating controller -Potentiometer unit (5k Ohm). -Three-positioning type for 110/220VAC (Choose three angular positions from 0°~270°.) |  |  |

| Model | Manual Override | Valve Mounting Flange (ISO 5211) |
| --- | --- | --- |
| JS-01~02 | Lever | F03, F04, F05, F07 |
| JS-03 | Lever | F05, F07 |
| JS-03H~06H | Hand Wheel | F07, F10, F12 |
| JS-06H-T08~10 | Hand Wheel | F10, F12 & F10, F14 |

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

The chart of the performance

- Standard ON/OFF Type

| Standard ON/OFF Type, 12VDC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle * | Maximum Operating Current | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 35 | 310 | 10-15 | 100% | 10A | 1.5A | F*-1.25A | 1.9 | 4.2 |
| JS-02 | 50 | 443 | 10-16 |  |  |  |  | 1.9 | 4.2 |

| Standard ON/OFF Type, 24VDC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle * | Maximum Operating Current | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 35 | 310 | 11-16 | 100% | 2.8A | 0.9A | F*-1.0A | 1.9 | 4.2 |
| JS-02 | 50 | 443 | 12-18 |  | 3.2A | 0.8A | F*-1.0A | 1.9 | 4.2 |
| JS-03 | 140 | 1238 | 7-13 |  | 5.4A | 2.6A | F*-3.0A | 3.9 | 8.6 |
| JS-03H* | 160 | 1416 | 10-15 |  |  |  |  | 6.9 | 15.2 |
| JS-04H* | 275 | 2434 | 27-47 |  |  |  |  | 7.6 | 16.8 |
| JS-06H-T08* | 800 | 7080 | 88-120 |  |  |  |  | 14 | 30.8 |

| Standard ON/OFF Type, 24VAC/DC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle * | Maximum Operating Current | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 35 | 310 | 11-16 | 100% | 2.8A | 0.9A | F*-0.8A | 1.9 | 4.2 |
| JS-02 | 50 | 443 | 12-18 |  | 3.2A | 0.8A |  | 1.9 | 4.2 |
| JS-03 | 140 | 1238 | 7-13 |  |  | 2.6A | F*-3.0A | 3.9 | 8.6 |
| JS-03H* | 160 | 1416 | 10-15 |  |  |  |  | 6.9 | 15.2 |
| JS-04H* | 275 | 2434 | 27-47 |  |  |  |  | 7.6 | 16.8 |
| JS-06H-T08* | 800 | 7080 | 88-120 |  |  |  |  | 14 | 30.8 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) H：In the part number indicates hand-wheel manual override.

(3) F：Fast acting fuse.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

| Standard ON/OFF Type, 110VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time ( sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01 | 35 | 310 | 12 | 10 | 20% 15min | 0.7A | TP* | 1.7 | 3.7 |
| JS-02 | 50 | 443 |  |  |  | 0.9A |  | 1.8 | 3.9 |
| JS-03 | 170 | 1505 | 10 | 8 | 50% 60min | 1.2A |  | 4.4 | 9.7 |
| JS-03H* | 200 | 1770 | 12 | 10 |  |  |  | 7.9 | 17.4 |
| JS-04H* | 380 | 3363 | 36 | 30 |  |  |  | 8.6 | 19.0 |
| JS-05H* | 500 | 4425 |  |  |  | 2.0A |  | 8.8 | 19.4 |
| JS-06H* | 600 | 5310 |  |  |  | 2.4A |  | 9.1 | 20.1 |
| JS-06H*-T08 | 1100 | 9735 | 106 | 88 |  | 2.0A |  | 14.5 | 31.9 |
| JS-06H*-T09 | 1500 | 13275 |  |  |  | 2.0A |  | 14.8 | 32.6 |
| JS-06H*-T10 | 1800 | 15930 |  |  |  | 2.8A |  | 15.2 | 33.5 |

| Standard ON/OFF Type, 220VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time ( sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01 | 35 | 310 | 12 | 10 | 20% 15min | 0.4A | TP* | 1.7 | 3.7 |
| JS-02 | 50 | 443 |  |  |  | 0.50A |  | 1.8 | 3.9 |
| JS-03 | 170 | 1505 | 10 | 8 | 50% 60min | 0.8A |  | 4.4 | 9.7 |
| JS-03H* | 200 | 1770 | 12 | 10 |  |  |  | 7.9 | 17.4 |
| JS-04H* | 380 | 3363 | 36 | 30 |  |  |  | 8.6 | 19.0 |
| JS-05H* | 500 | 4425 |  |  |  |  |  | 8.8 | 19.4 |
| JS-06H* | 600 | 5310 |  |  |  |  |  | 9.1 | 20.1 |
| JS-06H*-T08 | 1100 | 9735 | 106 | 88 |  | 1.0A |  | 14.5 | 31.9 |
| JS-06H*-T09 | 1500 | 13275 |  |  |  | 1.0A |  | 14.8 | 32.6 |
| JS-06H*-T10 | 1800 | 15930 |  |  |  | 1.1A |  | 15.2 | 33.5 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) H：In the part number indicates hand-wheel manual override.

(3) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

| Standard ON/OFF Type, 220VAC (3-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-03 | 170 | 1505 | 10 | 8 | 50% 60min | 0.7A | TP* | 4.4 | 9.7 |
| JS-03H* | 200 | 1770 | 12 | 10 |  |  |  | 7.9 | 17.4 |
| JS-04H* | 380 | 3363 | 36 | 30 |  |  |  | 8.6 | 19.0 |
| JS-05H* | 500 | 4425 | 36 | 30 |  | 0.9A |  | 8.8 | 19.4 |
| JS-06H* | 600 | 5310 | 36 | 30 |  |  |  | 9.1 | 20.1 |
| JS-06H*-T08 | 1100 | 9735 | 106 | 88 |  |  |  | 14.5 | 31.9 |
| JS-06H*-T10 | 1800 | 15930 | 106 | 88 |  |  |  | 15.2 | 33.5 |

| Standard ON/OFF Type, 380/440/460VAC (3-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-03 | 170 | 1505 | 10 | 8 | 50% 60min | 0.5A | TP* | 4.4 | 9.7 |
| JS-03H* | 200 | 1770 | 12 | 10 |  |  |  | 7.9 | 17.4 |
| JS-04H* | 380 | 3363 | 36 | 30 |  |  |  | 8.6 | 19.0 |
| JS-05H* | 500 | 4425 | 36 | 30 |  |  |  | 8.8 | 19.4 |
| JS-06H* | 600 | 5310 | 36 | 30 |  |  |  | 9.1 | 20.1 |
| JS-06H*-T08 | 1100 | 9735 | 106 | 88 |  |  |  | 14.5 | 31.9 |
| JS-06H*-T10 | 1800 | 15930 | 106 | 88 |  |  |  | 15.2 | 33.5 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) H：In the part number indicates hand-wheel manual override.

(3) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

- “Low Energy” ON/OFF Type

| “Low Energy” ON/OFF Type, 110VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01A | 32 | 283 | 19 | 16 | 100% | 0.2A | N/A | 1.7 | 3.7 |
| JS-02A | 36 | 319 | 20 | 17 | 40% 60min | 0.3A | TP* | 1.75 | 3.9 |
| JS-02A | 50 | 443 | 43 | 36 | 100% | 0.2A | N/A | 1.8 | 4.0 |
| JS-03A | 90 | 797 | 42 | 35 | 40% 60min | 0.3A | N/A | 3.5 | 7.7 |
| JS-03A | 120 | 1062 | 65 | 54 | 40% 60min | 0.3A | N/A | 3.5 | 7.7 |
| JS-03A | 100 | 885 | 65 | 54 | 100% | 0.2A | N/A | 3.5 | 7.7 |

| “Low Energy” ON/OFF Type, 220VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01A | 32 | 283 | 19 | 16 | 100% | 0.10A | N/A | 1.7 | 3.7 |
| JS-02A | 36 | 319 | 20 | 17 | 40% 60min | 0.15A | TP* | 1.75 | 3.9 |
| JS-02A | 50 | 443 | 43 | 36 | 100% | 0.10A | N/A | 1.8 | 4.0 |
| JS-03A | 90 | 797 | 42 | 35 | 40% 60min | 0.15A | N/A | 3.5 | 7.7 |
| JS-03A | 120 | 1062 | 65 | 54 | 40% 60min | 0.15A | N/A | 3.5 | 7.7 |
| JS-03A | 100 | 885 | 65 | 54 | 100% | 0.10A | N/A | 3.5 | 7.7 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

- “Fast Acting” ON/OFF Type

| “Fast Acting” ON/OFF Type, 12VDC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle* | Maximum Operating Current | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 10 | 89 | 1-2 | 100% | 10A | 3.3A | F*-3.0A | 1.9 | 4.2 |
| JS-01 | 25 | 221 | 3-6 |  |  | 2.5A | F*-2.0A | 1.9 | 4.2 |

| “Fast Acting” ON/OFF Type, 24VDC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle* | Maximum Operating Current | Rated Current | Overload protection device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 10 | 89 | 1-2 | 100% | 3.2A | 1.9A | F*-1.5A | 1.9 | 4.2 |
| JS-01 | 25 | 221 | 3-8 |  | 3.2A | 1.3A | F*-1.5A | 1.9 | 4.2 |
| JS-03 | 30 | 226 | 1-3 |  | 5.4A | 4A | F*-3.0A | 3.9 | 8.6 |
| JS-03 | 60 | 531 | 4-7 |  | 5.4A | 1.9A | F*-3.0A | 3.9 | 8.6 |

| “Fast Acting” ON/OFF Type, 24VAC/DC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) | Duty Cycle* | Maximum Operating Current | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in |  |  |  |  |  | kg | lbs |
| JS-01 | 10 | 89 | 1-2 | 100% | 3.2A | 1.9A | F*-1.5A | 1.9 | 4.2 |
| JS-01 | 25 | 221 | 3-8 |  | 3.2A | 1.3A | F*-1.5A | 1.9 | 4.2 |
| JS-03 | 30 | 226 | 1-3 |  | 5.4A | 4A | F*-3.0A | 3.9 | 8.6 |
| JS-03 | 60 | 531 | 4-7 |  | 5.4A | 1.9A | F*-3.0A | 3.9 | 8.6 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) F：Fast acting fuse.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836
                           Power Fang Enterprise Company Ltd

| “Fast Acting” ON/OFF Type, 110VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01 | 9 | 80 | 1.2 | 1 | 50% 60min | 1.2A | TP* | 1.9 | 4.2 |
| JS-01 | 25 | 221 | 4 | 3 |  |  |  | 1.9 | 4.2 |
| JS-03 | 35 | 310 | 1.2 | 1 |  |  |  | 3.9 | 8.6 |
| JS-03 | 100 | 885 | 6 | 5 |  |  |  | 3.9 | 8.6 |

| “Fast Acting” ON/OFF Type, 220VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle time (sec /90°) |  | Duty Cycle* | Rated Current | Overload protection device | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz |  | kg | lbs |
| JS-01 | 9 | 80 | 1.2 | 1 | 50% 60min | 0.38A | TP* | 1.9 | 4.2 |
| JS-01 | 25 | 221 | 4 | 3 |  | 0.60A |  | 1.9 | 4.2 |
| JS-03 | 35 | 310 | 1.2 | 1 |  | 0.72A |  | 3.9 | 8.6 |
| JS-03 | 100 | 885 | 6 | 5 |  | 0.72A |  | 3.9 | 8.6 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836
                     Power Fang Enterprise Company

- Modulation Type

The differences between AMD and BMD:

There are two differences of using of the motors between AMD and BMD. One AMD model runs with synchronous motors, the other BMD model runs with inductive motors.

There are two Comparison of AMD and BMD : AMD has lower power consumption which saves electricity. BMD has more powerful torque value and much faster.

| Modulation Type, 24VAC (1-Phase) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle * | Rated Current | Overload Protection Device |  | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz | MOTOR | PCB | kg | lbs |
| JS-01-AMD | 20 | 177 | 19 | 16 | 100% | 0.8A | F*-1.0A TP* | F*-0.5A | 2.1 | 4.6 |
| JS-02-AMD | 45 | 398 | 43 | 36 |  |  |  |  | 2.1 | 4.6 |
| JS-03-AMD | 75 | 664 | 42 | 35 |  |  |  |  | 3.7 | 8.2 |
| JS-03-AMD | 110 | 974 | 65 | 54 |  |  |  |  | 3.7 | 8.2 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) F：Fast acting fuse.

(3) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

| Modulation Type, 110VAC (1-Phase) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle * | Rated Current | Overload Protection device |  |  | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz | MOTOR | PCB |  | kg | lbs |
| JS-01-AMD | 25 | 221 | 19 | 16 | 100% | 0.2A | F*-0.5A TP* |  | F*-0.15A | 2.1 | 4.6 |
| JS-02-AMD | 36 | 319 | 19 | 16 | 50% 60min | 0.3A |  |  |  | 2.1 | 4.6 |
| JS-02-AMD | 50 | 443 | 43 | 36 | 100% | 0.2A |  |  |  | 2.1 | 4.6 |
| JS-03-AMD | 100 | 885 | 42 | 35 | 50% 60min | 0.3A |  |  |  | 3.7 | 8.2 |
| JS-03-AMD | 120 | 1062 | 65 | 54 |  | 0.3A |  |  |  | 3.7 | 8.2 |
| JS-03-BMD | 170 | 1505 | 10 | 8 |  | 1.2A | F*-1.5A TP* |  |  | 4.8 | 10.6 |
| JS-03H* -BMD | 200 | 1770 | 12 | 10 |  | 1.2A |  |  |  | 8.3 | 18.3 |
| JS-04H* -BMD | 300 | 2655 | 36 | 30 |  | 1.2A |  |  |  | 9.0 | 19.8 |
| JS-05H* -BMD | 500 | 4425 | 36 | 30 |  | 2.0A | F*-3.0A TP* |  |  | 9.2 | 20.3 |
| JS-06H* -BMD | 600 | 5310 | 36 | 30 |  | 2.4A |  |  |  | 9.5 | 20.9 |
| JS-06H* -BMD-T08 | 1100 | 9735 | 106 | 88 |  | 1.2A | F*-1.5A TP* |  |  | 14.5 | 31.9 |
| JS-06H* -BMD-T09 | 1500 | 13275 | 106 | 88 |  | 2.0A | F*-3.0A TP* |  |  | 14.8 | 32.6 |
| JS-06H* -BMD-T10 | 1800 | 15930 | 106 | 88 |  | 2.4A |  |  |  | 15.2 | 33.5 |

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

]                                                       Tel no.: 886 2 8283 9836

Power Fang Enterprise Company

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) H：In the part number indicates hand-wheel manual override

(3) F：Fast acting fuse.

(4) TP：Indicates motor thermal overload protector.

| Modulation Type, 220VAC (1-Phase) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* | Rated Current | Overload Protection Device |  | Weight |  |
|  | N·m | lbf·in | 50Hz | 60Hz |  | 50/60Hz | MOTOR | PCB | kg | lbs |
| JS-01-AMD | 25 | 221 | 19 | 16 | 100% | 0.10A | F*-0.25A TP* | F*-0.15A | 2.1 | 4.6 |
| JS-02-AMD | 36 | 319 | 19 | 16 | 50% 60min | 0.15A |  |  | 2.1 | 4.6 |
| JS-02-AMD | 50 | 443 | 43 | 36 | 100% | 0.10A |  |  | 2.1 | 4.6 |
| JS-03-AMD | 100 | 885 | 42 | 35 | 50% 60min | 0.15A |  |  | 3.7 | 8.2 |
| JS-03-AMD | 120 | 1062 | 65 | 54 |  | 0.15A |  |  | 3.7 | 8.2 |
| JS-03-BMD | 170 | 1505 | 10 | 8 |  | 0.72A | F*-1.0A TP* |  | 4.8 | 10.6 |
| JS-03H* -BMD | 200 | 1770 | 12 | 10 |  | 0.72A |  |  | 8.3 | 18.3 |
| JS-04H* -BMD | 300 | 2655 | 36 | 30 |  | 0.72A |  |  | 9.0 | 19.8 |
| JS-05H* -BMD | 500 | 4425 | 36 | 30 |  | 0.75A | F*-1.5A TP* |  | 9.2 | 20.3 |
| JS-06H* -BMD | 600 | 5310 | 36 | 30 |  | 0.80A |  |  | 9.5 | 20.9 |
| JS-06H* -BMD-T08 | 1100 | 9735 | 106 | 88 |  | 0.72A | F*-1.0A TP* |  | 14.5 | 31.9 |
| JS-06H* -BMD-T09 | 1500 | 13275 | 106 | 88 |  | 0.75A | F*-1.5A TP* |  | 14.8 | 32.6 |
| JS-06H* -BMD-T10 | 1800 | 15930 | 106 | 88 |  | 0.80A |  |  | 15.2 | 33.5 |

Note *

(1) Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

(2) H：In the part number indicates hand-wheel manual override

(3) F：Fast acting fuse.

(4) TP：Indicates motor thermal overload protector.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

“Battery Backup Fail-safe” ON/OFF Type

| “Battery Backup Fail-safe” ON/OFF Type, 12VDC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle Time (sec /90°) |  | Duty Cycle* |  | Rated Current (max) | Weight |  |
| JS-02-ECR | N·m | lbf·in | Normal | Power- off line | Normal | Power- off line | 0.8A (1.3A) | kg | lbs |
|  | 12 | 106 | 13-15 | 13-21 | 33% 1min | 8% 6min |  | 1.6 | 3.5 |

| “Battery Backup Fail-safe” ON/OFF Type, 24VAC/DC |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle time (sec /90°) |  | Duty Cycle* |  | Rated Current (max) | Weight |  |
| JS-02-ECR | N·m | lbf·in | Normal | Power- off line | Normal | Power- off line | 0.7A (1.3A) | kg | lbs |
|  | 12 | 106 | 13-15 | 13-21 | 33% 1min | 8% 6min |  | 1.6 | 3.5 |

| “Battery Backup Fail-safe” ON/OFF Type, 110VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle time (sec /90°) |  | Duty Cycle* |  | Rated Current 50/60HZ (max) | Weight |  |
| JS-02-ECR | N·m | lbf·in | Normal | Power- off line | Normal | Power- off line | 0.2A (0.3A) | kg | lbs |
|  | 12 | 106 | 13-15 | 13-21 | 33% 1min | 8% 6min |  | 1.6 | 3.5 |

| “Battery Backup Fail-safe” ON/OFF Type, 220VAC (1-Phase) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | Torque |  | Cycle time (sec /90°) |  | Duty Cycle* |  | Rated Current 50/60HZ (max) | Weight |  |
| JS-02-ECR | N·m | lbf·in | Normal | Power- off line | Normal | Power- off line | 0.1A (0.2A) | kg | lbs |
|  | 12 | 106 | 13-15 | 13-21 | 33% 1min | 8% 6min |  | 1.6 | 3.5 |

Note *

- Duty Cycle：The definition of Duty Cycle is in accordance with IEC60034-S4 duty type.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

- Wiring Diagram

110/220VAC (1-Phase)

N L

12VDC, 24VDC

24VAC/DC

Auxiliary switch (optional)

220/380/440/460VAC (3-Phase)

Auxiliary switch (optional) Power Fang Enterprise Company Ltd e-mail : pfpf01@gmail.com What’s App : 886 955789002 Tel no.: 886 2 8283 9836

“Modulation” Type, AMD Board 24/110/220VAC

Motor Fuse Board Fuse (0.15A/250V) (0-5 VDC, 0-5 VDC, 1-5 VDC, 1-5 VDC, 0-10 VDC, 0-10 VDC) (4-20 mA, 4-20 mA, 2-10 mA, 2-10 mA) Auxiliary switch (optional) (Optional)

“Modulation” Type, BMD Board 110/220VAC

Board Fuse (0.15A/250V) (0-5 VDC, 0-5 VDC, 1-5 VDC, 1-5 VDC, 0-10 VDC, 0-10 VDC) (4-20 mA, 4-20 mA, 2-10 mA, 2-10 mA) Auxiliary switch (optional)

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Signal Flow of Modulation Type

Switch & Adjustment Settings

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

“Battery Backup Fail-safe” Type, 110/220VAC, 12VDC and 24VAC/DC

Power-Off Mode Setting. Setting method; Action mode. Connect A with B; The actuator will be switched ON in power-off status.. Connect B with C; The actuator will be switched OFF in power-off status.. Auxiliary switch (optional) *The functional contact point(4-NC, 4-NO, 4-COM) and the functional contact point(3-NC, 3-NO, 3-COM) are the auxiliary switch with the capacity of AC220V/0.1A.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

DIMENSIONS

| JS-01~02 |  | Flange type: F03, F04, F05, F07 |
| --- | --- | --- |
| Unit: mm |  |  |
| JS-03 | Flange type: F05, F07 |  |
| Unit: mm |  |  |
| JS-03H~06H | Flange type: F07, F10, F12 |  |
| Unit: mm |  |  |
| JS-06H-T08~T10 | Flange type:F10, F12&F10, F14 |  |
| Unit: mm |  |  |

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836

Power Fang Enterprise Company Ltd

JS - Series Actuator To Valve Selection Chart

| Model No. | Valve Type | Valve Size(inch) | Valve Material |
| --- | --- | --- | --- |
| JS-01 | Screwed Ends Ball Valve | 1/2”~1-1/2” | SUS316/PVC/PP |
| JS-02 | Screwed Ends Ball Valve | 1/2”~2” | SUS316/PVC/PP |
| JS-03 | Screwed Ends Ball Valve | 1-1/4”~ 3” | SUS316/PVC/PP |
| JS-03H | Screwed Ends Ball Valve | 1-1/2”~3” | SUS316/PVC/PP |
| JS-01 | Socket Welded Ends Ball Valve | 1/2”~1-1/2” | PVC/PP |
| JS-02 | Socket Welded Ends Ball Valve | 1/2”~2” | PVC/PP |
| JS-03 | Socket Welded Ends Ball Valve | 2”~ 3” | PVC/PP |
| JS-03H | Socket Welded Ends Ball Valve | 2”~ 3” | PVC/PP |
| JS-04H | Socket Welded Ends Ball Valve | 4” | PVC/PP |
| JS-01 | Flanged Ends Ball Valve | 1/2”~1” | Cast Iron/SUS304/SUS316 |
| JS-02 | Flanged Ends Ball Valve | 1-1/4”~2” | Cast Iron/SUS304/SUS316 |
| JS-03 | Flanged Ends Ball Valve | 1-1/4”~3” | Cast Iron/SUS304/SUS316 |
| JS-03H | Flanged Ends Ball Valve | 1-1/4”~3” | Cast Iron/SUS304/SUS316 |
| JS-04H | Flanged Ends Ball Valve | 4” | Cast Iron/SUS304/SUS316 |
| JS-05H | Flanged Ends Ball Valve | 5” | Cast Iron/SUS304/SUS316 |
| JS-06H | Flanged Ends Ball Valve | 6” | Cast Iron/SUS304/SUS316 |
| JS-01 | 3-Way Screwed Ends Ball Valve | 1/2”~1” | SUS316 |
| JS-02 | 3-Way Screwed Ends Ball Valve | 1-1/4”~1-1/2” | SUS316 |
| JS-03 | 3-Way Screwed Ends Ball Valve | 1-1/4”~2” | SUS316 |
| JS-02 | 3-Way Flanged Ends Ball Valve | 1” | Cast Iron/SUS304/SUS316 |
| JS-03 | 3-Way Flanged Ends Ball Valve | 1-1/2”~2” | Cast Iron/SUS304/SUS316 |
| JS-03H | 3-Way Flanged Ends Ball Valve | 1-1/2”~2-1/2” | Cast Iron/SUS304/SUS316 |
| JS-04H | 3-Way Flanged Ends Ball Valve | 3” | Cast Iron/SUS304/SUS316 |
| JS-05H | 3-Way Flanged Ends Ball Valve | 4” | Cast Iron/SUS304/SUS316 |
| JS-06H | 3-Way Flanged Ends Ball Valve | 5” | Cast Iron/SUS304/SUS316 |
| JS-02 | Butterfly Valve | 2”~3” | Cast Iron/SUS304/SUS316 |
| JS-03 | Butterfly Valve | 2”~5” | Cast Iron/SUS304/SUS316 |
| JS-03H | Butterfly Valve | 2”~6” | Cast Iron/SUS304/SUS316 |
| JS-04H | Butterfly Valve | 8” | Cast Iron/SUS304/SUS316 |
| JS-05H | Butterfly Valve | 10” | Cast Iron/SUS304/SUS316 |
| JS-06H | Butterfly Valve | 10” | Cast Iron/SUS304/SUS316 |

Notes:

- Please check valve torque before mounting.

- Please check working pressure, service fluid, and temperature.

Power Fang Enterprise Company Ltd

e-mail : pfpf01@gmail.com

What’s App : 886 955789002

Tel no.: 886 2 8283 9836